## Sheet1
Date | 18/1 | 19/1 | 20/1 | 21/1 | 2016-01-22 | 2016-01-23 | 2016-01-24 | 2016-01-25 | 2016-01-26 | 2016-01-27 | 2016-01-28 | 2016-01-29 | 2016-01-30 | 2016-01-31 | 2016-02-01 | 2016-02-02 | 2016-02-03 | 2016-02-04 | 2016-02-05 | 2016-02-06 | 2016-02-07 | 2016-02-08 | 2016-02-09 | 2016-02-10 | 2016-02-11 | 2016-02-12 | 2016-02-13 | 2016-02-14 | 2016-02-15 | 2016-02-16 | 2016-02-17 | 2016-02-18 | 2016-02-19 | 2016-02-20 | 2016-02-21 | 2016-02-22 | 2016-02-23 | 2016-02-24 | 2016-02-25 | 2016-02-26 | 2016-02-27 | 2016-02-28 | 2016-02-29
Event and key actions taken | Contact with the Metropolitan Redevelopment Authority (MRA) to discuss the Elizabeth Quay (EQ) Water Spray Park (WSP). | DOH officers inspect WSP and identify 13 issues to be completed before opening – written advice sent to Leighton |  | City of Perth takes sample. Balance Tank Cl ppm: 2.1ppm Temp: 26C Response from Leighton to advice from DOH on 19 Jan 16 | 2016-01-25: City of Perth takes sample. Balance tank chlorine: 1.63ppm Temp: 30C; 2016-01-26: City of Perth takes BACKWASH sample. Backwash chlorine: 5.9ppm Temp: 31.1C; 2016-01-28: City of Perth takes sample. Balance tank chlorine: 3.89ppm Temp: 27.6C DoH advised that Leighton have appointed a trained technical operator to oversee WSP operations; 2016-01-29: EHD advised by Leighton about progress with compliance issues identified in correspondence from EHD to Leighton on 19 Jan 16. DOH issued a Permit to Operate to MRA at 2.54pm.; 2016-02-01: DOH called meeting at EQ WSP with constructors & MRA to discuss need for remedial action.; 2016-02-02: EHD staff met with the MRA and consultants at EQ to discuss further improvements to the operating systems and facility. Issues identified included: • Improving drainage. • Divert first run off each day to sewer. • Balance tank to operate at 2mg/l free chlorine. • Removal of layer of debris at bottom of balance tank. • Separate sample point for each filter.; 2016-02-04: WSP closed by operator for cleaning, maintenance and additional works.; 2016-02-05: City of Perth takes sample. Balance tank chlorine: "High" Temp: Not recorded - Bashwash 2 Temp: 29.6C Operator opened park for a few hours in the morning, but advised by DOH to close pending a clean set of microbiology results; 2016-02-08: Backwash number 5 cleaned and superchlorinated MRA advised at noon they could re-open the facility.; 2016-02-12: City of Perth takes sample. Balance tank chlorine: 3.47ppm Temp: 27.8C; 2016-02-18: City of Perth takes sample. Balance tank chlorine: 5.09ppm Temp: 24.6C; 2016-02-22: EHD advised MRA to close the WSP; 2016-02-26: City of Perth takes sample. Balance tank chlorine: 4.82ppm Temp: 26C
WSP superchlorinated overnight to the extent that would kill all Naegleria species
Park Operation | Park Not Opened | Park Not Opened | Park Not Opened | Park Not Opened | Park Not Opened | Park Not Opened | Park Not Opened | Park Not Opened | Park Not Opened | Park Not Opened | Park Not Opened | Park Open | Park Open | Park Open | Park Open | Park Open | Park Open | Park Closed | Park Closed | Park Closed | Park Closed | Park Open | Park Open | Park Open | Park Open | Park Open | Park Open | Park Open | Park Open | Park Open | Park Open | Park Open | Park Open | Park Open | Park Open | Park Closed | Park Closed | Park Closed | Park Closed | Park Closed | Park Closed | Park Closed | Park Closed
Sample taken on 21 January 2016
Backwash (W16-005465) |  |  |  |  | 2016-01-22: E. coli ALL CLEAR & Naegleria Pending; 2016-01-25: E. coli ALL CLEAR Naegleria DETECTED; 2016-01-28: E. coli ALL CLEAR & N. fowleri NEGATIVE
Balance Tank (W16-005466) |  |  |  |  | 2016-01-22: E. coli ALL CLEAR & Naegleria Pending; 2016-01-25: E.coli and Naegleria ALL CLEAR; 2016-01-28: E.coli & Naegleria ALL CLEAR
Sample taken on 25 January 2016
Backwash (W16-005868) |  |  |  |  | 2016-01-27: E. coli ALL CLEAR & Naegleria Pending; 2016-01-28: E.coli & Naegleria ALL CLEAR; 2016-02-01: E. coli & Naegleria ALL CLEAR
Balance Tank (W16-005869) |  |  |  |  | 2016-01-27: E. coli ALL CLEAR & Naegleria Pending; 2016-01-28: E. coli ALL CLEAR & Naegleria DETECTED; 2016-02-01: E. coli ALL CLEAR & N. fowleri NEGATIVE
Sample taken on 26 January 2016
Backwash (W16-005931) |  |  |  |  | 2016-01-27: E. coli ALL CLEAR & Naegleria Pending; 2016-01-29: E. coli ALL CLEAR & Naegleria DETECTED; 2016-02-01: E. coli ALL CLEAR & N. fowleri NEGATIVE
Sample taken on 28 January 2016
Trough 3 (W16-006747) |  |  |  |  | 2016-01-29: E. coli ALL CLEAR & Naegleria Pending; 2016-02-01: E.coli & Naegleria ALL CLEAR; 2016-02-05: E.coli AND Naegleria ALL CLEAR
Trough 4 (W16-006746) |  |  |  |  | 2016-01-29: E. coli ALL CLEAR & Naegleria Pending; 2016-02-01: E.coli & Naegleria ALL CLEAR; 2016-02-05: E.coli AND Naegleria ALL CLEAR
Balance Tank (W16-006748) |  |  |  |  | 2016-01-29: E. coli ALL CLEAR & Naegleria Pending; 2016-02-01: E.coli & Naegleria ALL CLEAR; 2016-02-05: E.coli AND Naegleria ALL CLEAR
Backwash (W16-006749) |  |  |  |  | 2016-01-29: E. coli ALL CLEAR & Naegleria Pending; 2016-02-01: E. coli ALL CLEAR & Naegleria DETECTED; 2016-02-05: E. coli ALL CLEAR & N. fowleri NEGATIVE
Sample taken on 5 February 2016
Trough 3 (W16-008958) |  |  |  |  | 2016-02-06: E. coli ALL CLEAR & Naegleria Pending; 2016-02-08: E. coli AND Naegleria ALL CLEAR
Trough 4 (W16-008959) |  |  |  |  | 2016-02-06: E. coli ALL CLEAR & Naegleria Pending; 2016-02-08: E. coli AND Naegleria ALL CLEAR
Balance Tank (W16-008960) |  |  |  |  | 2016-02-06: E. coli ALL CLEAR & Naegleria Pending; 2016-02-08: E. coli AND Naegleria ALL CLEAR
Backwash 1 (W16-008961) |  |  |  |  | 2016-02-06: E. coli ALL CLEAR & Naegleria Pending; 2016-02-08: E. coli AND Naegleria ALL CLEAR; 2016-02-10: E. coli AND Naegleria ALL CLEAR
Backwash 2 (W16-008962) |  |  |  |  | 2016-02-06: E. coli ALL CLEAR & Naegleria Pending; 2016-02-08: E. coli AND Naegleria ALL CLEAR; 2016-02-10: E. coli AND Naegleria ALL CLEAR
Backwash 3 (W16-008963) |  |  |  |  | 2016-02-06: E. coli ALL CLEAR & Naegleria Pending; 2016-02-08: E. coli AND Naegleria ALL CLEAR; 2016-02-10: E. coli AND Naegleria ALL CLEAR
Backwash 4 (W16-008964) |  |  |  |  | 2016-02-06: E. coli ALL CLEAR & Naegleria Pending; 2016-02-08: E. coli AND Naegleria ALL CLEAR; 2016-02-10: E. coli AND Naegleria ALL CLEAR
Backwash 5 (W16-008965) |  |  |  |  | 2016-02-06: E. coli ALL CLEAR & Naegleria Pending; 2016-02-08: E. coli AND Naegleria ALL CLEAR; 2016-02-10: E. coli AND Naegleria ALL CLEAR
Backwash 6 (W16-008966) |  |  |  |  | 2016-02-06: E. coli ALL CLEAR & Naegleria Pending; 2016-02-08: E. coli AND Naegleria ALL CLEAR; 2016-02-10: E. coli AND Naegleria ALL CLEAR
Sample taken on 12 February 2016
Trough 3 (W16-010743) |  |  |  |  | 2016-02-13: E. coli ALL CLEAR & Pseu AND Naegleria Pending; 2016-02-14: E. coli ALL CLEAR & Pseu 20 cfu/100mL & Naegleria Pending; 2016-02-15: E. coli AND Naegleria ALL CLEAR & Pseu 20 cfu/100mL
Trough 4 (W16-010744) |  |  |  |  | 2016-02-13: E. coli ALL CLEAR & Pseu AND Naegleria Pending; 2016-02-14: E. coli ALL CLEAR & Pseu 1 cfu/100mL & Naegleria Pending; 2016-02-15: E. coli AND Naegleria ALL CLEAR & Pseu 1 cfu/100mL
Balance Tank (W16-010742) |  |  |  |  | 2016-02-13: E. coli ALL CLEAR & Pseu AND Naegleria Pending; 2016-02-14: E. coli AND Pseu ALL CLEAR & Naegleria Pending; 2016-02-15: E. coli AND Pseu AND Naegleria ALL CLEAR
Backwash 1 (W16-010736) |  |  |  |  | 2016-02-13: E. coli ALL CLEAR & Pseu AND Naegleria Pending; 2016-02-14: E. coli ALL CLEAR & Pseu 1 cfu/100mL & Naegleria Pending; 2016-02-15: E. coli AND Naegleria ALL CLEAR & Pseu 1 cfu/100mL
Backwash 2 (W16-010737) |  |  |  |  | 2016-02-13: E. coli ALL CLEAR & Pseu AND Naegleria Pending; 2016-02-14: E. coli ALL CLEAR & Pseu 28 cfu/100mL & Naegleria Pending; 2016-02-15: E. coli AND Naegleria ALL CLEAR & Pseu 28 cfu/100mL
Backwash 3 (W16-010738) |  |  |  |  | 2016-02-13: E. coli ALL CLEAR & Pseu AND Naegleria Pending; 2016-02-14: E. coli ALL CLEAR & Pseu 12 cfu/100mL & Naegleria Pending; 2016-02-15: E. coli AND Naegleria ALL CLEAR & Pseu 12 cfu/100mL
Backwash 4 (W16-010739) |  |  |  |  | 2016-02-13: E. coli ALL CLEAR & Pseu AND Naegleria Pending; 2016-02-14: E. coli ALL CLEAR & Pseu >100 cfu/100mL & Naegleria Pending; 2016-02-15: E. coli AND Naegleria ALL CLEAR & Pseu >100 cfu/100mL
Backwash 5 (W16-010740) |  |  |  |  | 2016-02-13: E. coli ALL CLEAR & Pseu AND Naegleria Pending; 2016-02-14: E. coli ALL CLEAR & Pseu >100 cfu/100mL & Naegleria Pending; 2016-02-15: E. coli AND Naegleria ALL CLEAR & Pseu >100 cfu/100mL
Backwash 6 (W16-010741) |  |  |  |  | 2016-02-13: E. coli ALL CLEAR & Pseu AND Naegleria Pending; 2016-02-14: E. coli ALL CLEAR & Pseu >100 cfu/100mL & Naegleria Pending; 2016-02-15: E. coli AND Naegleria ALL CLEAR & Pseu >100 cfu/100mL
Scheme Water (W16-010745) |  |  |  |  | 2016-02-13: E. coli ALL CLEAR & Pseu AND Naegleria Pending; 2016-02-14: E. coli and Pseu ALL CLEAR & Naegleria Pending; 2016-02-15: E. coli AND Pseu AND Naegleria ALL CLEAR
Sample taken on 18 February 2016
Trough 1 (W16-012518) |  |  |  |  | 2016-02-22: E.coli AND Naegleria ALL CLEAR & Pseu 8 cfu/100mL
Trough 2 (W16-012519) |  |  |  |  | 2016-02-22: E.coli AND Naegleria ALL CLEAR & Pseu 16 cfu/100mL
Trough 3 (W16-012520) |  |  |  |  | 2016-02-22: E.coli AND Naegleria ALL CLEAR & Pseu 11 cfu/100mL
Trough 4 (W16-012521) |  |  |  |  | 2016-02-22: E.coli AND Naegleria ALL CLEAR & Pseu 15 cfu/100mL
Balance Tank (W16-012517) |  |  |  |  | 2016-02-22: E.coli AND Naegleria ALL CLEAR & Pseu 3 cfu/100mL
Backwash 1 (W16-012511) |  |  |  |  | 2016-02-22: E.coli AND Naegleria ALL CLEAR & Pseu 90 cfu/100mL; 2016-02-24: E.coli AND Naegleria ALL CLEAR & Pseu 90 cfu/100mL
Backwash 2 (W16-012512) |  |  |  |  | 2016-02-22: E.coli ALL CLEAR & Pseu 45 cfu/100mL & Naegleria DETECTED; 2016-02-24: E.coli ALL CLEAR & Pseu 45 cfu/100mL & N. fowleri NEGATIVE
Backwash 3 (W16-012513) |  |  |  |  | 2016-02-22: E.coli ALL CLEAR & Pseu 33 cfu/100mL & Naegleria DETECTED; 2016-02-24: E.coli ALL CLEAR & Pseu 33 cfu/100mL & N. fowleri NEGATIVE
Backwash 4 (W16-012514) |  |  |  |  | 2016-02-22: E.coli AND Naegleria ALL CLEAR & Pseu >100 cfu/100mL; 2016-02-24: E.coli AND Naegleria ALL CLEAR & Pseu >100 cfu/100mL
Backwash 5 (W16-012515) |  |  |  |  | 2016-02-22: E.coli AND Naegleria ALL CLEAR & Pseu >100 cfu/100mL; 2016-02-24: E.coli AND Naegleria ALL CLEAR & Pseu >100 cfu/100mL
Backwash 6 (W16-012516) |  |  |  |  | 2016-02-22: E.coli AND Naegleria ALL CLEAR & Pseu 11 cfu/100mL; 2016-02-24: E.coli AND Naegleria ALL CLEAR & Pseu 11 cfu/100mL
Sample taken on 26 February 2016
Backwash 1 (W16-014382) |  |  |  |  | 2016-02-29: E.coli AND Naegleria AND Pseu ALL CLEAR
Backwash 2 (W16-014383) |  |  |  |  | 2016-02-29: E.coli AND Naegleria ALL CLEAR & Pseu 5 cfu/100mL
Backwash 3 (W16-014384) |  |  |  |  | 2016-02-29: E.coli AND Naegleria ALL CLEAR & Pseu 22 cfu/100mL
Backwash 4 (W16-014385) |  |  |  |  | 2016-02-29: E.coli AND Naegleria ALL CLEAR & Pseu 15 cfu/100mL
Backwash 5 (W16-014386) |  |  |  |  | 2016-02-29: E.coli AND Naegleria ALL CLEAR & Pseu 9 cfu/100mL
Backwash 6 (W16-014387) |  |  |  |  | 2016-02-29: E.coli AND Naegleria ALL CLEAR & Pseu 5 cfu/100mL
Balance Tank (W16-014388) |  |  |  |  | 2016-02-29: E.coli AND Naegleria AND Pseu ALL CLEAR
Trough 1 (W16-014389) |  |  |  |  | 2016-02-29: E.coli AND Naegleria ALL CLEAR & Pseu 41 cfu/100mL
Trough 2 (W16-014390) |  |  |  |  | 2016-02-29: E.coli AND Naegleria ALL CLEAR & Pseu 27cfu/100mL
Trough 3 (W16-014391) |  |  |  |  | 2016-02-29: E.coli AND Naegleria AND Pseu ALL CLEAR
Trough 4 (W16-014392) |  |  |  |  | 2016-02-29: E.coli AND Naegleria ALL CLEAR & Pseu 28 cfu/100mL
NB: Samples were taken on the dates stated in red text in the left column and the dates the Department of Health were made aware of the results is within the table. (NEW RESULTS IN BOLD) Note that trough samples are subject to cross-contamination The term Naegleria refers to generic Naegleria. Samples positive for generic Naegleria are then subject to further analysis to determine whether the disease-causing Naegleria fowleri is present
Park Not Opened
Park Open
Sample of concern but NOT requiring immediate public health action
Sample required IMMEDIATE closure of facility
Sample required IMMEDIATE Public Health action
Results ALL CLEAR
Park temporarily
open